## Upgrade to VFD Chiller
Cooling Equipment Upgrade to Chiller w/VFD
Existing Cooling Equipment |  |  | Proposed Cooling Equipment
2 Carrier 19XR Chillers - Constant Speed |  | D/X, Chiller, District Cooling |  | VFD Chiller
Total Connected Tons: | 1100 |  |  | Total Connected Tons: | 1100
Assumed Design Tons: | 1100 |  |  | Assumed Design Tons: | 1100
Area
Cooling Assumptions |  |  |  | SqFt
Sensible Heat Ratio: |  | i.e., 60%, 70%, 80%, etc. |  | 501120
Design IAT: |  |  | Chiller Efficacy Curve Points
| Existing Occupied IAT | 72 |  | w/o VFD | w/ VFD
| Existing Unoccupied IAT | 78 | % Load | kW/Ton | kW/Ton
| Proposed Occupied IAT | 72 | 30% | 0.828 | 0.375
| Proposed Unoccupied IAT | 78 | 70% | 0.55 | 0.301
|  |  | 100% | 0.476 | 0.406
Existing |  |  |  | Proposed
Electricity Cost | 0.12793 | per kWh (w/Demand) |  | Electricity Cost |  | per kWh (w/Demand)
| OR |  |  |  | OR
Electricity Cost |  | per kWh (w/o Demand) |  | Electricity Cost |  | per kWh (w/o Demand)
Electric Demand Cost |  | per kW |  | Electric Demand Cost |  | per kW